# Ozonation: Model Formulation and Calculation Procedure

This note documents, step by step, how the ozonation unit (OzoneDPRZO, ozone_DPR_zo.py; wired in DPR_flowsheet_v4.py) determines its design and operating variables and how each quantity is computed. It mirrors the level of detail of the Supplementary Text S6 and states the exact equations, constants, and degrees-of-freedom logic implemented in the code.

Notation: r = O3:TOC mass ratio (mg O₃ / mg TOC); τ = hydraulic retention time HRT (min); k = first-order ozone-decay constant (min⁻¹); C₃₀ = ozone residual 30 s after application (mg/L); CT = disinfection exposure (mg·min/L); LRV = log reduction value; Q = feed volumetric flow; D = applied ozone dose (mg/L); η = ozone mass-transfer efficiency; SEC = specific energy of ozone generation.

# 1. Role and treatment objectives

Ozonation is the lead barrier of the DPR advanced-treatment train. It is designed for two objectives, and conditions the water for the downstream biologically active carbon (BAC):

Pathogen inactivation — quantified through the CT (concentration × time) concept. Cryptosporidium is the most ozone-resistant of the three regulated pathogens, so the process is sized around the Cryptosporidium log-reduction target; achieving ≥ 1-log Cryptosporidium concurrently yields ≥ 6-log for viruses and Giardia.

CEC oxidation — the O3:TOC ratio controls removal of the performance surrogates carbamazepine and sulfamethoxazole; an O3:TOC of 0.5–1.0 gives ≥ 1-log removal while keeping bromate below its 10 µg/L MCL.

Ozone does not remove TOC (removal fraction = 0); it transforms bulk organics into more biodegradable forms for the BAC. The two design handles are therefore the O3:TOC ratio r and the contactor HRT τ.

# 2. Design variables and operating envelope

| Quantity | Symbol | Range / value | Set where |
| --- | --- | --- | --- |
| O3:TOC ratio | r | 0.5 – 1.0 (California fixed at 1.0) | free variable / bound |
| Contact time (HRT) | τ | 5 – 15 min (SI: contactor HRT ≤ 15 min) | free variable / bound |
| Mass-transfer efficiency | η | 1.0 | database (yaml) |
| Specific energy | SEC | 5 kWh/lb | database (yaml) |
| Required Crypto LRV | LRV | 1 – 3 (from DPR_initial_setting) | config |

Both r and τ are free variables linked by the CT relationship below; the flowsheet optimizer (minimizing LCOW) selects the cost-optimal point on that curve. Because ozone capital scales with τ, the optimizer drives τ toward its lower feasible bound.

# 3. Governing CT relationship

Ozone decay is treated as biphasic: an instantaneous ozone demand (IOD) consumes ozone over the first 30 s, after which the residual decays by an apparent first-order reaction. Three empirical relationships close the model.

(a) Decay constant k as a function of r and effluent type (linear fits of the Gerrity data over r = 0.5–1.0):

k = −0.6422·r + 0.8342     (tertiary effluent)        (1a)

k = −0.2637·r + 0.5251     (secondary effluent)        (1b)

Secondary effluent has a higher TOC load and therefore faster ozone decay (larger k), which later makes a given CT harder to reach.

(b) Ozone residual 30 s after application (Pang et al., 2023; linear in r between 0.5 and 1.0):

C₃₀ = 0.704·r + 1.136     [mg/L]        (2)

(c) CT achieved over the contactor. The residual sits at C₃₀ through the 30-s IOD window and then decays first-order to the end of the HRT. Integrating the residual gives:

CT(τ) = C₃₀ · [ 0.5 + (1 − e^(−k(τ−0.5))) / k ]     [mg·min/L]        (3)

The term 0.5·C₃₀ is the exposure during the first 0.5 min; the second term is ∫ C₃₀ e^(−k(t−0.5)) dt from 0.5 to τ. Equation (3) is implemented as the CT_achieved expression in the model.

# 4. Required CT and LRV crediting

The required exposure for the Cryptosporidium credit is linear in the target log reduction:

CT_req = 2.47 · LRV     [mg·min/L]        (4)

The required LRV is set upstream by DPR_initial_setting from the state regulation minus the fixed credits of the other barriers (e.g. California Crypto 15 − UF 4 − RO 2 − UV/AOP 6 = 3, capped at the 6-log single-barrier maximum). Viruses and Giardia are credited 6-log whenever the Crypto CT is met, so only the Crypto CT constrains the ozone design.

# 5. Determination of the O3:TOC ratio

Two candidate O3:TOC values are formed by inverting the CT relationship, then combined with regulatory floors.

(i) O3:TOC needed to meet the Cryptosporidium CT. Setting CT(τ) = CT_req and solving (2)–(3) for r:

expr1 = ( CT_req·k / [0.5·k + (1 − e^(−k(τ−0.5)))] − 1.136 ) / 0.704        (5)

(ii) O3:TOC needed to hold a 0.2 mg/L ozone residual at the outlet (Colorado only). Requiring C₃₀·e^(−k(τ−0.5)) = 0.2 mg/L and inverting (2):

expr2 = ( 0.2 / e^(−k(τ−0.5)) − 1.136 ) / 0.704        (6)

(iii) Selection by state. The design O3:TOC is the largest binding requirement, subject to a lower floor (a smooth maximum is used in code for differentiability):

California:      r = 1.0        (7a)

Colorado:        r = max( expr1 , expr2 , 0.5 )        (7b)

Florida / Arizona:  r = max( expr1 , 0.5 )        (7c)

California mandates the most stringent design, so r is pinned at 1.0 regardless of expr1; the CT target is then carried by the HRT (Section 6). For the other states r follows the binding requirement with a 0.5 floor — the minimum recommended dose. Because k depends on r through (1), equations (5)–(7) are implicit in r and are solved simultaneously by the optimizer (no per-effluent polynomial fit is needed; secondary and tertiary are handled by the same equations through their k).

# 6. Contact time for California (in-model determination)

Because California fixes r = 1.0, the dose no longer adjusts to meet the CT; the HRT must. The model therefore sets τ so the achieved CT equals the requirement, floored at the 5-min design minimum:

CT(τ) = max( CT_req , CT(τ = 5 min) )        (8)

If 5 min already exceeds CT_req the right-hand side is CT(5) and τ = 5 min; otherwise the right-hand side is CT_req and τ is driven up until the Cryptosporidium CT is exactly met. This is the ca_hrt_ct_constraint equality in the model; it fully determines τ for California with no flowsheet-side CT constraint. For the other states τ stays a free optimization variable and the LCOW objective pushes it to the lower bound while r follows (5)–(7).

# 7. Ozone dose, mass flow, and energy

Once r is known, the applied ozone dose adds the TOC-driven demand and the nitrite demand (nitrite consumes ozone 1:1 on a molar basis and is expressed on a nitrogen basis):

D = TOC · r / η  +  [NO₂ as N]     [mg/L]        (9)

ṁ(O₃) = Q · D     [lb/hr]        (10)

P = SEC · ṁ(O₃)     [kW]        (11)

with η = 1.0 and SEC = 5 kWh/lb from the database. Nitrite is converted from NO₂ to N by the factor 14.0067 / 46.0055. The ozone mass flow and power feed the costing and energy accounting (capital scales with τ and dose).

# 8. Degrees of freedom and solution sequence

The ozone unit contributes the following free variables and constraints:

Variables: r (O3:TOC) and τ (HRT), plus dose D, ozone mass flow, and power.

Constraints: the O3:TOC equation (7) [and, for California, the HRT equation (8)]; the dose (9); mass flow (10); and power (11).

Solution sequence per solve:

1. The required Crypto LRV → CT_req from (4).

2. k(r) from (1) for the effluent type.

3. For CO/FL/AZ: r is pinned by (7) to the minimum dose meeting CT (and residual); the optimizer chooses τ (minimizing LCOW) with r following. For CA: r = 1.0 and (8) determines τ.

4. D from (9), then mass flow (10) and power (11).

Initialization fixes τ = 5 min for the square solve in all states except California, where τ is left free (equation 8 determines it); the optimization stage frees τ within [5, 15] min and, for non-CA states, r within [0.5, 1.0].

# 9. Worked examples (10 MGD, tertiary unless noted)

| Scenario | LRV | k (min⁻¹) | τ (min) | O3:TOC | CT (mg·min/L) | Binding |
| --- | --- | --- | --- | --- | --- | --- |
| CA / RBAT | 3 | 0.192 | 6.39 | 1.000 | 7.41 = CT_req | eq.(8) HRT |
| CA / RBAT (secondary) | 3 | 0.261 | 10.26 | 1.000 | 7.41 = CT_req | eq.(8) HRT |
| CO / RBAT | 1 | 0.455 | 5.00 | 0.590 | 3.74 (>CT_req) | expr2 residual |
| FL / RBAT | 1 | 0.513 | 5.00 | 0.500 | 3.36 (>CT_req) | 0.5 floor |
| FL / CBAT | 2 | 0.322 | 5.00 | 0.806 | 4.94 = CT_req | expr1 CT |

Reading the first row: California requires 3-log Crypto (CT_req = 7.41). With r = 1.0, C₃₀ = 1.84 mg/L and k = 0.192 min⁻¹; equation (8) raises τ to 6.39 min, at which CT(τ) = 7.41 exactly. Secondary effluent decays faster (k = 0.261), so the same 3-log target needs τ = 10.26 min — a longer, costlier contactor. Colorado’s residual requirement (expr2) makes it the binding term there, lifting r to 0.59 even though the 1-log CT alone would need less.

Feed-flow independence: the ozone design (τ, r) is unchanged from 2 to 100 MGD, because equations (1)–(8) depend on the TOC concentration, the required LRV, and τ — not on the volumetric flow. Only the ozone mass flow (10) and power (11) scale with Q.

# 10. Parameters and constants

| Parameter | Value | Unit | Source |
| --- | --- | --- | --- |
| CT credit slope (Crypto) | 2.47 | mg·min/L per log | code |
| k, tertiary | −0.6422·r + 0.8342 | min⁻¹ | code (Gerrity fit) |
| k, secondary | −0.2637·r + 0.5251 | min⁻¹ | code (Gerrity fit) |
| C₃₀ vs r (Pang 2023) | 0.704·r + 1.136 | mg/L | code |
| O3:TOC lower floor | 0.5 | – | code |
| O3:TOC, California | 1.0 (fixed) | – | code |
| HRT bounds | 5 – 15 | min | flowsheet / SI |
| Outlet residual (CO) | 0.2 | mg/L | code |
| Mass-transfer efficiency η | 1.0 | – | yaml |
| Specific energy SEC | 5 | kWh/lb | yaml (Mundy 2018) |
| Nitrite → N factor | 14.0067 / 46.0055 | – | code |

# 11. Notes

Secondary vs. tertiary are handled by the same equations through k (1a/1b); no separate polynomial fit is required. This is the key change from the earlier polynomial model (OzoneDPRZOv0), whose contact_time polynomials were fit to the tertiary k only.

Physical feasibility: the maximum achievable Crypto LRV at r = 1.0 and τ = 15 min is ≈ 3.6 log (tertiary) and ≈ 3.0 log (secondary). A required LRV above this makes the problem infeasible (the O3:TOC equation would need r > 1.0, or the CA CT equation cannot be met), which surfaces as a solve failure rather than a silent under-design.

Bromate is not modeled as an explicit constraint; keeping r within 0.5–1.0 holds bromate below its MCL by construction.