# Ozonation: Model Formulation and Calculation Procedure (v2)

Version 2 (July 2026). Change vs. v1: the Colorado 0.2 mg/L ozone-residual term (expr2) has been removed — that residual requirement does not apply to ozone under the CO regulation — so Colorado is now treated like the other non-California states (O3:TOC = max(expr1, 0.5)). The residual term is retained, commented out, in the code so it can be re-enabled if needed.

This note documents, step by step, how the ozonation unit (OzoneDPRZO, ozone_DPR_zo.py; wired in DPR_flowsheet_v4.py) determines its design and operating variables and how each quantity is computed. It mirrors the level of detail of the Supplementary Text S6.

Notation: r = O3:TOC mass ratio (mg O₃ / mg TOC); τ = HRT (min); k = first-order ozone-decay constant (min⁻¹); C₃₀ = ozone residual 30 s after application (mg/L); CT = exposure (mg·min/L); LRV = log reduction value; Q = feed flow; D = applied ozone dose (mg/L); η = mass-transfer efficiency; SEC = specific energy of ozone generation.

# 1. Role and treatment objectives

Ozonation is the lead barrier of the DPR advanced-treatment train. It is designed for two objectives and conditions the water for the downstream biologically active carbon (BAC):

Pathogen inactivation — quantified through the CT (concentration × time) concept. Cryptosporidium is the most ozone-resistant of the three regulated pathogens, so the process is sized around the Cryptosporidium log-reduction target; achieving ≥ 1-log Cryptosporidium concurrently yields ≥ 6-log for viruses and Giardia.

CEC oxidation — the O3:TOC ratio controls removal of the performance surrogates carbamazepine and sulfamethoxazole; an O3:TOC of 0.5–1.0 gives ≥ 1-log removal while keeping bromate below its 10 µg/L MCL.

Ozone does not remove TOC (removal fraction = 0); it transforms bulk organics into more biodegradable forms for the BAC. The two design handles are the O3:TOC ratio r and the contactor HRT τ.

# 2. Design variables and operating envelope

| Quantity | Symbol | Range / value | Set where |
| --- | --- | --- | --- |
| O3:TOC ratio | r | 0.5 – 1.0 (California fixed at 1.0) | free variable / bound |
| Contact time (HRT) | τ | 5 – 15 min (SI: contactor HRT ≤ 15 min) | free variable / bound |
| Mass-transfer efficiency | η | 1.0 | database (yaml) |
| Specific energy | SEC | 5 kWh/lb | database (yaml) |
| Required Crypto LRV | LRV | 1 – 3 (from DPR_initial_setting) | config |

Both r and τ are free variables linked by the CT relationship below; the flowsheet optimizer (minimizing LCOW) selects the cost-optimal point on that curve. Because ozone capital scales with τ, the optimizer drives τ toward its lower feasible bound.

# 3. Governing CT relationship

Ozone decay is treated as biphasic: an instantaneous ozone demand (IOD) consumes ozone over the first 30 s, after which the residual decays by an apparent first-order reaction. Three empirical relationships close the model.

(a) Decay constant k as a function of r and effluent type (linear fits of the Gerrity data over r = 0.5–1.0):

k = −0.6422·r + 0.8342     (tertiary effluent)        (1a)

k = −0.2637·r + 0.5251     (secondary effluent)        (1b)

Secondary effluent has a higher TOC load and therefore faster ozone decay (larger k), which later makes a given CT harder to reach.

(b) Ozone residual 30 s after application (Pang et al., 2023; linear in r between 0.5 and 1.0):

C₃₀ = 0.704·r + 1.136     [mg/L]        (2)

(c) CT achieved over the contactor. The residual sits at C₃₀ through the 30-s IOD window and then decays first-order to the end of the HRT. Integrating the residual gives:

CT(τ) = C₃₀ · [ 0.5 + (1 − e^(−k(τ−0.5))) / k ]     [mg·min/L]        (3)

The term 0.5·C₃₀ is the exposure during the first 0.5 min; the second term is ∫ C₃₀ e^(−k(t−0.5)) dt from 0.5 to τ. Equation (3) is implemented as the CT_achieved expression in the model.

# 4. Required CT and LRV crediting

The required exposure for the Cryptosporidium credit is linear in the target log reduction:

CT_req = 2.47 · LRV     [mg·min/L]        (4)

The required LRV is set upstream by DPR_initial_setting from the state regulation minus the fixed credits of the other barriers (e.g. California Crypto 15 − UF 4 − RO 2 − UV/AOP 6 = 3, capped at the 6-log single-barrier maximum). Viruses and Giardia are credited 6-log whenever the Crypto CT is met, so only the Crypto CT constrains the ozone design.

# 5. Determination of the O3:TOC ratio

The O3:TOC needed to meet the Cryptosporidium CT is obtained by inverting the CT relationship. Setting CT(τ) = CT_req and solving (2)–(3) for r:

expr1 = ( CT_req·k / [0.5·k + (1 − e^(−k(τ−0.5)))] − 1.136 ) / 0.704        (5)

Selection by state. The design O3:TOC is the CT requirement subject to a lower floor (a smooth maximum is used in code for differentiability):

California:            r = 1.0        (6a)

Colorado / Florida / Arizona:   r = max( expr1 , 0.5 )        (6b)

California mandates the most stringent design, so r is pinned at 1.0 regardless of expr1; the CT target is then carried by the HRT (Section 6). For every other state r follows the CT requirement with a 0.5 floor — the minimum recommended dose. Because k depends on r through (1), equation (5) is implicit in r and is solved simultaneously by the optimizer (no per-effluent polynomial fit is needed; secondary and tertiary are handled by the same equation through their k).

Note — Colorado residual (removed in v2). v1 of this model added a second candidate for Colorado, the O3:TOC needed to hold a 0.2 mg/L ozone residual at the contactor outlet, expr2 = (0.2·e^(k(τ−0.5)) − 1.136)/0.704, and used r = max(expr1, expr2, 0.5). On review, that 0.2 mg/L residual requirement does not apply to ozone under the Colorado regulation, so expr2 is disabled (kept commented in the code) and Colorado now uses equation (6b) like the other non-CA states.

# 6. Contact time for California (in-model determination)

Because California fixes r = 1.0, the dose no longer adjusts to meet the CT; the HRT must. The model therefore sets τ so the achieved CT equals the requirement, floored at the 5-min design minimum:

CT(τ) = max( CT_req , CT(τ = 5 min) )        (7)

If 5 min already exceeds CT_req the right-hand side is CT(5) and τ = 5 min; otherwise the right-hand side is CT_req and τ is driven up until the Cryptosporidium CT is exactly met. This is the ca_hrt_ct_constraint equality in the model; it fully determines τ for California with no flowsheet-side CT constraint. For the other states τ stays a free optimization variable and the LCOW objective pushes it to the lower bound while r follows equations (5)–(6).

# 7. Ozone dose, mass flow, and energy

Once r is known, the applied ozone dose adds the TOC-driven demand and the nitrite demand (nitrite consumes ozone 1:1 on a molar basis and is expressed on a nitrogen basis):

D = TOC · r / η  +  [NO₂ as N]     [mg/L]        (8)

ṁ(O₃) = Q · D     [lb/hr]        (9)

P = SEC · ṁ(O₃)     [kW]        (10)

with η = 1.0 and SEC = 5 kWh/lb from the database. Nitrite is converted from NO₂ to N by the factor 14.0067 / 46.0055. The ozone mass flow and power feed the costing and energy accounting (capital scales with τ and dose).

# 8. Degrees of freedom and solution sequence

The ozone unit contributes the following free variables and constraints:

Variables: r (O3:TOC) and τ (HRT), plus dose D, ozone mass flow, and power.

Constraints: the O3:TOC equation (6) [and, for California, the HRT equation (7)]; the dose (8); mass flow (9); and power (10).

Solution sequence per solve:

1. The required Crypto LRV → CT_req from (4).

2. k(r) from (1) for the effluent type.

3. For CO/FL/AZ: r is pinned by (6b) to the minimum dose meeting CT; the optimizer chooses τ (minimizing LCOW) with r following. For CA: r = 1.0 and (7) determines τ.

4. D from (8), then mass flow (9) and power (10).

Initialization fixes τ = 5 min for the square solve in all states except California, where τ is left free (equation 7 determines it); the optimization stage frees τ within [5, 15] min and, for non-CA states, r within [0.5, 1.0].

# 9. Worked examples (10 MGD, tertiary unless noted)

| Scenario | LRV | k (min⁻¹) | τ (min) | O3:TOC | CT (mg·min/L) | Binding |
| --- | --- | --- | --- | --- | --- | --- |
| CA / RBAT | 3 | 0.192 | 6.39 | 1.000 | 7.41 = CT_req | eq.(7) HRT |
| CA / RBAT (secondary) | 3 | 0.261 | 10.26 | 1.000 | 7.41 = CT_req | eq.(7) HRT |
| CO / RBAT | 1 | 0.513 | 5.00 | 0.500 | 3.36 (>CT_req) | 0.5 floor |
| FL / RBAT | 1 | 0.513 | 5.00 | 0.500 | 3.36 (>CT_req) | 0.5 floor |
| FL / CBAT | 2 | 0.322 | 5.00 | 0.806 | 4.94 = CT_req | expr1 CT |

Reading the first row: California requires 3-log Crypto (CT_req = 7.41). With r = 1.0, C₃₀ = 1.84 mg/L and k = 0.192 min⁻¹; equation (7) raises τ to 6.39 min, at which CT(τ) = 7.41 exactly. Secondary effluent decays faster (k = 0.261), so the same 3-log target needs τ = 10.26 min — a longer, costlier contactor. With the CO residual removed (v2), Colorado now matches Florida/Arizona: a 1-log requirement is met at the 0.5 floor with τ = 5 min (previously the residual term lifted CO to r ≈ 0.59).

Feed-flow independence: the ozone design (τ, r) is unchanged from 2 to 100 MGD, because equations (1)–(7) depend on the TOC concentration, the required LRV, and τ — not on the volumetric flow. Only the ozone mass flow (9) and power (10) scale with Q.

# 10. Parameters and constants

| Parameter | Value | Unit | Source |
| --- | --- | --- | --- |
| CT credit slope (Crypto) | 2.47 | mg·min/L per log | code |
| k, tertiary | −0.6422·r + 0.8342 | min⁻¹ | code (Gerrity fit) |
| k, secondary | −0.2637·r + 0.5251 | min⁻¹ | code (Gerrity fit) |
| C₃₀ vs r (Pang 2023) | 0.704·r + 1.136 | mg/L | code |
| O3:TOC lower floor | 0.5 | – | code |
| O3:TOC, California | 1.0 (fixed) | – | code |
| HRT bounds | 5 – 15 | min | flowsheet / SI |
| Outlet residual (CO) | 0.2 (disabled in v2 — see §5) | mg/L | code (commented) |
| Mass-transfer efficiency η | 1.0 | – | yaml |
| Specific energy SEC | 5 | kWh/lb | yaml (Mundy 2018) |
| Nitrite → N factor | 14.0067 / 46.0055 | – | code |

# 11. Notes

v2 change: the Colorado 0.2 mg/L ozone-residual term (expr2) is disabled; it does not apply to ozone under the CO regulation. The lines remain commented in O3toTOC_ratio_constraint and can be re-enabled to restore r = max(expr1, expr2, 0.5) for Colorado.

Secondary vs. tertiary are handled by the same equations through k (1a/1b); no separate polynomial fit is required. This is the key change from the earlier polynomial model (OzoneDPRZOv0), whose contact_time polynomials were fit to the tertiary k only.

Physical feasibility: the maximum achievable Crypto LRV at r = 1.0 and τ = 15 min is ≈ 3.6 log (tertiary) and ≈ 3.0 log (secondary). A required LRV above this makes the problem infeasible, which surfaces as a solve failure rather than a silent under-design.

Bromate is not modeled as an explicit constraint; keeping r within 0.5–1.0 holds bromate below its MCL by construction.